## Sheet1
Access Control Commissioning Checklist
Door Locks and Hardware
Physical Operation, For every controlled opening:
| • | Check all lock / hardware fasteners or mounts are secure and without play, slack, or gaps exceeding tolerances on installation instructions. | -
| • | Ensure operation of lock is free of binding, grinding, or interference for door or frame features or other components. | -
| • | Close and open door, or operate several cycles, the opening to ensure that no binding or warping is affecting operation. | -
| • | If Exit Devices are used, confirm appropriate 'Push to Exit' signage is displayed. | -
| • | If Door Closers or Operators are used, confirm electronic access devices do not interfere with operation. | -
| • | Confirm secure installation and function of Door Position Switches/ Contacts/ DPS. | -
| • | Weatherproof and lightly apply grease per specification to mechanical hardware like hinges | -
| • | Ensure any cabling or system wiring is hidden, tucked behind raceway or frames, and is not being pinched or cut. | -
| • | Confirm that accessibility clearances are satisfied and any additional access control devices comply with codes. | -
| • | If standalone, battery powered locks are used, confirm remaining battery life is strong and document commission date of batteries for future reference. | -
Door Controller Install Checks
| • | Confirm that all terminated wiring at controller is secured and terminated without short for each device. | -
| • | If kept in a metal enclosure, ensure panel tamper contacts and panel locks are used. Gather panel keys for central, secure management | -
| • | If controllers are located at the door, confirm they are installed on the secure/locked side of the opening and located behind a tamper-resistant or semi-obscured location | -
| • | For wireless locks, confirm that all hubs or repeaters are clearly labeled as companions to the separate system readers or controllers. | -
Free Egress and Fire Alarm Loop Check
| • | Confirm that upon fire alarm activation, all door maglocks release and are not powered. | -
| • | Confirm that upon fire alarm activation, all emergency exit doors and openings can be freely opened and are not locked for any reason. | -
| • | Confirm that during normal operating conditions, all 'Request To Exit' devices are located in code compliant arrangements and function properly | -
| • | Check that any delayed egress openings have specifically been approved by the AHJ, and delays do not exceed 15 seconds, unless specifically excepted by AHJ. | -
| • | Confirm that all Pushbutton style RTE switches are properly labeled and displayed per local code requirements, and directly interrupt power to locks and not controller, unless specifically excepted by AHJ. | -
Credential Reader Checks:
| • | Confirm that reader device is securely anchored without gaps to the wall, frame, post, or bollard. Seal or install trim guards where needed. | -
| • | Confirm 'normal operation' status lights are displayed per intended behavior. (On/Off/Red/Green/Blue, etc.) | -
| • | Confirm audible beep or siren registers when credential is read. | -
| • | Check that reader tamper device is connected and configured. | -
| • | If contactless type reader, present test card to confirm read range meets spec. | -
| • | If biometric type reader, confirm unit positioning will not be interfered with by environmental features (ie: sun movement, HVAC downdrafts, etc) | -
| • | Confirm that accessibility clearances are satisfied and any additional access control devices comply with codes. | -
Credential Enrollment:
| • | Confirm that the only credentials to be immediately carried/used by cardholders are activated, and no preemptive or batched activation of unissued/ stored credentials is done. | -
| • | Check that each user issued a credential is accurately classified and identified in the access control software. Include Picture ID images if possible. | -
| • | If credentials are being renewed or exchanged, confirm physical possession, disposal, and deactivation of old credential in system. | -
| • | If biometric credentials are enrolled, confirm multiple digits or templates are enrolled. | -
| • | If multi-factor credentials are issued, confirm that all factors are recorded, active, and valid in the system. | -
Access Management Software Servers
Access Management Software Configuration
| • | Configure Unlock, Extended unlock, Door Hold Open, and Relock event periods, as appropriate. | -
| • | Configure user access schedules (e.g., 24/7, 8am-5pm, off-hours, holidays, etc.) | -
| • | Configure user access levels (e.g., Managers, Workers, Visitors, Temporaries, etc.) | -
| • | Confirm Polling Interval, or settings update push duration as prompt and as close to real-time to be accurate as recorded in system. | -
| • | Configure any Maps or floorplans used to display and manage system control points. | -
| • | Confirm successful integration and configuration of features like 'Video Verification', or integration with video surveillance, intrusion, fire alarm, and intercom systems. | -
| • | Configure alarm or event notifications (email, text, etc.) | -
| • | Download and retain copies of all door/controller configurations | -
| • | Confirm any imported databases are clean and without problems if populating access management system. | -
| • | For 'Anti-Passback' rules, ensure that users will not unwittingly or inadvertently cause alarms if they use atypical or uncontrolled openings. | -
Network/Security Settings
| • | Document Controller and other ethernet-based devices MAC address | -
| • | Assign and document Controller and other ethernet-based device IP address | -
| • | Update firmware to latest version (or manufacturer recommended/tested if different) | -
| • | Change Controller admin password from default | -
| • | Create multiple users if required (by specification or manufacturer recommendation) | -
| • | Set NTP server and verify time and date | -
| • | Disable unused services/close unused ports (FTP, telnet, SSH, etc.) | -
Hardware/Security
| • | Document MAC address(es) (often more than one if using multiple network cards), or if hosted/cloud access is used, document hostnames of all remote servers. | -
| • | Assign and document IP address(es) of every networked device, endpoint, or server. | -
| • | Apply latest OS updates (unless not recommended by manufacturer) | -
| • | Create secure admin password | -
| • | Create additional users as specified | -
| • | Test UPS operation and runtime (if supplied) | -
General Server Settings
| • | Confirm any requisite services or policies are free to operate and will restore automatically after reboot events. | -
| • | Change admin password from default | -
| • | Create operator/user logins | -
| • | If LDAP or Active Directory is used, confirm valid implementation and provisioning of service. | -
| • | Confirm and document any external database connections or dependencies by the access software. | -
Workstations
| • | Document MAC address(es) of each workstation | -
| • | Assign and document IP address(es) | -
| • | Apply latest OS updates (unless not recommended by manufacturer) | -
| • | Create secure admin password | -
| • | Create additional users as specified | -
| • | If dongles or hardware keys are required for client access, document location of key on workstation (e.g., Port Location, Key Serial Number) | -
Network
| • | Document MAC address(es) of each device | -
| • | Assign IP address and document | -
| • | Update switch/firewall/router firmware to latest version | -
| • | Change admin password from default | -
| • | Configure VLAN(s) as required | -
| • | Configure QoS as required | -
| • | Disable unused switch ports as specified | -
| • | Configure SNMP monitoring if required | -
| • | Configure MAC filtering if required | -
| • | Download and retain configuration for each switch | -
| • | Test UPS operation and runtime for each switch (if supplied) | -
Cabling
| • | Label all cables, patch panels, wall outlets, etc., as specified | -
| • | Ensure cables are secured to supports (J-hooks, ceiling truss, etc.) | -
| • | Conceal cables where possible/required | -
| • | Leave properly coiled and dressed service loops at controller location and head end as required | -
| • | Test all terminations and document results as specified | -
| • | Document cable test results as specified (if certification is required) | -